## Curve Data
Chiller Performance Curves
| Air Cooled Chiller in DOE Prototype for Secondary School 90.1-2010 |  |  | Ice Tank Charging and Discharging Curves |  | Water Cooled Chiller in DOE Prototype for Large Office 90.1-2010
Curve Name | AirCooled_Chiller_2010_PathA_CAPFT | AirCooled_Chiller_2010_PathA_EIRFT | AirCooled_Chiller_AllCapacities_2004_2010_EIRFPLR | Curve Quadratic Linear 1 | Curve Quadratic Linear 2 | WaterCooled_PositiveDisplacement_Chiller_GT150_2010_PathA_CAPFT | WaterCooled_PositiveDisplacement_Chiller_GT150_2010_PathA_EIRFT | ChlrWtrCentPathAAllEIRRatio_fQRatio
Curve Type | CAPFT | EIRFT | EIRPLR | Charge | Discharge | CAPFT | EIRFT | EIRPLR
Function Type | Biquadratic | Biquadratic | Quadratic | Quadratic Linear | Quadratic Linear | Biquadratic | Biquadratic | Quadratic
Var x | Tcwls | Tcwle | PLR | Pc | Pd | Tcwls | Tcwle | PLR
min x | 5 | 5 | 0 | 0 | 0 | 5 | 5 | 0.1
max x | 10 | 10 | 1 | 1 | 1 | 10 | 10 | 1
Var y | Tconde | Tconde | N/A | LMTD* | LMTD* | Tconde | Tconde | N/A
min y | 12.7 | 12.7 | N/A | 0 | 0 | 17.78 | 17.78 | N/A
max y | 51.67 | 51.67 | N/A | 9.9 | 9.9 | 46.11 | 46.11 | N/A
c1 | 1.0434 | 0.59619 | 0.141 | 0 | 0 | 0.90612 | 0.37731 | 0.22215
c2 | 0.040707 | -0.0099496 | 0.655 | 0.09 | 0.09 | 0.029228 | -0.022903 | 0.50316
c3 | 0.0004506 | 0.0007888 | 0.203 | -0.15 | -0.15 | -0.0003647 | 0.0016504 | 0.2569
c4 | -0.0041514 | 0.0004506 | N/A | 6.12 | 6.12 | -0.0009709 | 0.011816 | N/A
c5 | -8.86e-05 | 0.0004875 | N/A | -0.324 | -0.324 | -9.05e-05 | 0.0004345 | N/A
c6 | -0.0003467 | -0.0007623 | N/A | -0.216 | -0.216 | 0.0002527 | -0.0010132 | N/A
min output | N/A | N/A | 0 | N/A | N/A | N/A | N/A | 0.28
max output | N/A | N/A | 1 | N/A | N/A | N/A | N/A | 1
output | CAPFT | EIRFT | EIRPLR | q* | q* | CAPFT | EIRFT | EIRPLR
Inputs Key:
Tcwls | Chilled water leaving setpoint temperature (Supply water temp SP)
Tcwl | Chilled water leaving temperature (Supply water temp)
Tconde | Condenser entering fluid temperature (Temp of water leaving cooling tower - for water cooled systems, Drybulb temp - for air cooled, Wetbulb temp - for evap cooled)
PLR | Chiller Part Load Ratio = cooling load/chiller's available cooling capacity, max(0, min(Q_evap/Q_avail, PLR_max))
Pc | Percent Charged (Ice tank state of charge (SOC))
Pd | Percent Discharged (1 - SOC)
LMTD* | Non-dimensionalized log-mean temperature difference across ice tank HX
Outputs Key:
CAPFT | Chiller cooling capacity factor, equal to 1 at reference conditions
EIRFT | Enegy input to cooling output factor, equal to 1 at reference conditions
EIRPLR | Energy input to cooling output factor, equal to 1 at reference conditions
q* | Non-dimensionalized instantaneous heat transfer rate
Other Variables:
Q_avail | available chiller capacity adjusted for current fluid temps, Q_avail = Q_ref*CAPFT
Q_ref | chiller capacity at reference conditions (nominal values)
CyclingRatio | min(PLR/PLR_min, 1.0), used when PLR is less than PLR_min (eg. 0.15)
Equations:
P_chiller | Q_avail*(1/COP_ref)*EIRFT*EIRPLR*CyclingRatio
CAPFT | c1 + c2*Tcwls + c3*Tcwls^2 + c4*Tconde + c5*Tconde^2 + c6*Tcwls*Tconde
EIRFT | c1 + c2*Tcwl + c3*Tcwl^2 + c4*Tconde + c5*Tconde^2 + c6*Tcwl*Tconde
EIRPLR | c1 + c2*PLR + c3*PLR^2
Charge | (c1 + c2*Pc + c3*Pc^2) + (c4 + c5*Pc + c6*Pc)*LMTD*
Discharge | (c1 + c2*Pd + c3*Pd^2) + (c4 + c5*Pd + c6*Pd)*LMTD*

## CAPFT
CAPFT Curve Data Tables
y = Tconde, entering (to condenser) outdoor air drybulb temperature [C]
x = Tcwls, chilled water leaving temperature setpoint [C]
AirCooled_Chiller_2010_PathA_CAPFT
x
|  | -6.111 | -5 | -4.4 | -3.89 | -2 | 0 | 5 | 5.5 | 6 | 6.5 | 6.667 | 7 | 7.5 | 8 | 8.333 | 8.5 | 9 | 9.5 | 10
| -4 | 0.81816 | 0.85937 | 0.88208 | 0.90164 | 0.97618 | 1.0586 | 1.2803 | 1.3037 | 1.3274 | 1.3512 | 1.3592 | 1.3753 | 1.3996 | 1.4242 | 1.4406 | 1.4489 | 1.4739 | 1.4991 | 1.5246
| 0 | 0.81145 | 0.85111 | 0.87299 | 0.89185 | 0.96377 | 1.0434 | 1.2582 | 1.2809 | 1.3038 | 1.327 | 1.3348 | 1.3504 | 1.374 | 1.3979 | 1.4139 | 1.422 | 1.4462 | 1.4708 | 1.4955
y | 4.44 | 0.80068 | 0.83863 | 0.85959 | 0.87766 | 0.94667 | 1.0232 | 1.2303 | 1.2523 | 1.2744 | 1.2968 | 1.3044 | 1.3195 | 1.3423 | 1.3654 | 1.3809 | 1.3887 | 1.4122 | 1.436 | 1.4599
| 5 | 0.79907 | 0.83681 | 0.85765 | 0.87562 | 0.94427 | 1.0204 | 1.2265 | 1.2484 | 1.2705 | 1.2928 | 1.3003 | 1.3153 | 1.3381 | 1.361 | 1.3765 | 1.3842 | 1.4077 | 1.4313 | 1.4552
| 7 | 0.79288 | 0.82984 | 0.85027 | 0.86789 | 0.93522 | 1.01 | 1.2126 | 1.2342 | 1.2559 | 1.2778 | 1.2852 | 1.3 | 1.3224 | 1.3451 | 1.3603 | 1.3679 | 1.391 | 1.4143 | 1.4378
| 9 | 0.78598 | 0.82217 | 0.84218 | 0.85945 | 0.92547 | 0.99884 | 1.198 | 1.2192 | 1.2406 | 1.2622 | 1.2695 | 1.284 | 1.3061 | 1.3284 | 1.3433 | 1.3509 | 1.3736 | 1.3966 | 1.4198
| 11 | 0.77837 | 0.81379 | 0.83339 | 0.8503 | 0.91501 | 0.987 | 1.1827 | 1.2035 | 1.2246 | 1.2458 | 1.253 | 1.2673 | 1.289 | 1.311 | 1.3257 | 1.3331 | 1.3555 | 1.3782 | 1.401
| 12.7 | 0.77134 | 0.80611 | 0.82535 | 0.84196 | 0.90556 | 0.97637 | 1.1692 | 1.1897 | 1.2104 | 1.2314 | 1.2384 | 1.2526 | 1.274 | 1.2956 | 1.3102 | 1.3175 | 1.3396 | 1.3619 | 1.3845
| 14 | 0.76562 | 0.79989 | 0.81887 | 0.83525 | 0.89799 | 0.9679 | 1.1584 | 1.1787 | 1.1992 | 1.22 | 1.227 | 1.241 | 1.2621 | 1.2836 | 1.298 | 1.3052 | 1.3271 | 1.3492 | 1.3715
| 15 | 0.76102 | 0.79491 | 0.81367 | 0.82987 | 0.89197 | 0.96118 | 1.15 | 1.1701 | 1.1904 | 1.211 | 1.2179 | 1.2318 | 1.2528 | 1.2741 | 1.2883 | 1.2955 | 1.3172 | 1.3392 | 1.3613
| 16 | 0.75624 | 0.78974 | 0.8083 | 0.82432 | 0.88576 | 0.95428 | 1.1413 | 1.1613 | 1.1815 | 1.2019 | 1.2087 | 1.2225 | 1.2433 | 1.2644 | 1.2786 | 1.2857 | 1.3072 | 1.329 | 1.3509
| 17 | 0.75129 | 0.7844 | 0.80275 | 0.8186 | 0.87938 | 0.9472 | 1.1325 | 1.1523 | 1.1723 | 1.1925 | 1.1993 | 1.213 | 1.2337 | 1.2545 | 1.2686 | 1.2757 | 1.297 | 1.3186 | 1.3404
| 18 | 0.74615 | 0.77888 | 0.79702 | 0.81269 | 0.87282 | 0.93995 | 1.1235 | 1.1431 | 1.163 | 1.183 | 1.1898 | 1.2033 | 1.2238 | 1.2445 | 1.2585 | 1.2655 | 1.2866 | 1.3081 | 1.3297
| 19 | 0.74084 | 0.77319 | 0.79112 | 0.80661 | 0.86608 | 0.93252 | 1.1144 | 1.1338 | 1.1535 | 1.1733 | 1.18 | 1.1934 | 1.2138 | 1.2343 | 1.2481 | 1.2551 | 1.2761 | 1.2973 | 1.3188
| 20 | 0.73535 | 0.76731 | 0.78504 | 0.80035 | 0.85917 | 0.92491 | 1.105 | 1.1243 | 1.1438 | 1.1635 | 1.1701 | 1.1834 | 1.2036 | 1.2239 | 1.2376 | 1.2445 | 1.2654 | 1.2864 | 1.3077
| 21 | 0.72969 | 0.76126 | 0.77878 | 0.79392 | 0.85208 | 0.91713 | 1.0955 | 1.1146 | 1.1339 | 1.1534 | 1.16 | 1.1732 | 1.1932 | 1.2134 | 1.227 | 1.2338 | 1.2545 | 1.2753 | 1.2965
| 22 | 0.72385 | 0.75503 | 0.77234 | 0.78731 | 0.84481 | 0.90917 | 1.0858 | 1.1047 | 1.1239 | 1.1432 | 1.1497 | 1.1628 | 1.1826 | 1.2026 | 1.2161 | 1.2229 | 1.2434 | 1.2641 | 1.285
| 23 | 0.71783 | 0.74863 | 0.76573 | 0.78052 | 0.83737 | 0.90103 | 1.076 | 1.0947 | 1.1137 | 1.1328 | 1.1393 | 1.1522 | 1.1719 | 1.1917 | 1.2051 | 1.2118 | 1.2321 | 1.2527 | 1.2734
| 24 | 0.71163 | 0.74205 | 0.75894 | 0.77355 | 0.82974 | 0.89272 | 1.0659 | 1.0845 | 1.1033 | 1.1223 | 1.1287 | 1.1415 | 1.161 | 1.1806 | 1.1939 | 1.2006 | 1.2207 | 1.2411 | 1.2616
| 25 | 0.70525 | 0.73529 | 0.75197 | 0.76641 | 0.82195 | 0.88422 | 1.0557 | 1.0741 | 1.0927 | 1.1115 | 1.1179 | 1.1306 | 1.1499 | 1.1694 | 1.1825 | 1.1891 | 1.2091 | 1.2293 | 1.2497
| 26 | 0.6987 | 0.72835 | 0.74483 | 0.75908 | 0.81397 | 0.87555 | 1.0453 | 1.0635 | 1.0819 | 1.1006 | 1.1069 | 1.1195 | 1.1386 | 1.1579 | 1.1709 | 1.1775 | 1.1973 | 1.2173 | 1.2375
| 27 | 0.69197 | 0.72124 | 0.7375 | 0.75159 | 0.80581 | 0.86671 | 1.0347 | 1.0527 | 1.071 | 1.0895 | 1.0957 | 1.1082 | 1.1271 | 1.1463 | 1.1592 | 1.1657 | 1.1853 | 1.2052 | 1.2252
| 28 | 0.68507 | 0.71395 | 0.73001 | 0.74391 | 0.79748 | 0.85768 | 1.0239 | 1.0418 | 1.0599 | 1.0782 | 1.0844 | 1.0968 | 1.1155 | 1.1345 | 1.1473 | 1.1537 | 1.1732 | 1.1928 | 1.2127
| 29 | 0.67799 | 0.70648 | 0.72233 | 0.73606 | 0.78898 | 0.84848 | 1.013 | 1.0307 | 1.0486 | 1.0668 | 1.0729 | 1.0851 | 1.1037 | 1.1225 | 1.1352 | 1.1416 | 1.1609 | 1.1803 | 1.2001
| 30 | 0.67073 | 0.69883 | 0.71448 | 0.72803 | 0.78029 | 0.8391 | 1.0019 | 1.0194 | 1.0372 | 1.0551 | 1.0612 | 1.0733 | 1.0917 | 1.1104 | 1.1229 | 1.1293 | 1.1484 | 1.1677 | 1.1872
| 31 | 0.66329 | 0.69101 | 0.70645 | 0.71982 | 0.77143 | 0.82954 | 0.99061 | 1.008 | 1.0255 | 1.0433 | 1.0493 | 1.0613 | 1.0796 | 1.0981 | 1.1105 | 1.1168 | 1.1357 | 1.1548 | 1.1742
| 32 | 0.65567 | 0.68301 | 0.69824 | 0.71144 | 0.76239 | 0.81981 | 0.97914 | 0.99631 | 1.0137 | 1.0313 | 1.0373 | 1.0492 | 1.0673 | 1.0856 | 1.0979 | 1.1041 | 1.1228 | 1.1418 | 1.161
| 33 | 0.64788 | 0.67483 | 0.68985 | 0.70287 | 0.75317 | 0.8099 | 0.9675 | 0.9845 | 1.0017 | 1.0192 | 1.025 | 1.0368 | 1.0547 | 1.0729 | 1.0851 | 1.0912 | 1.1098 | 1.1286 | 1.1476
| 34 | 0.63991 | 0.66648 | 0.68129 | 0.69413 | 0.74378 | 0.79981 | 0.95568 | 0.9725 | 0.98955 | 1.0068 | 1.0126 | 1.0243 | 1.0421 | 1.06 | 1.0721 | 1.0782 | 1.0966 | 1.1152 | 1.1341
| 35 | 0.63177 | 0.65795 | 0.67255 | 0.68522 | 0.73421 | 0.78955 | 0.94368 | 0.96033 | 0.97721 | 0.99431 | 1.0001 | 1.0116 | 1.0292 | 1.047 | 1.0589 | 1.065 | 1.0832 | 1.1017 | 1.1203
| 36 | 0.62344 | 0.64924 | 0.66364 | 0.67613 | 0.72446 | 0.77911 | 0.9315 | 0.94798 | 0.96468 | 0.98161 | 0.98732 | 0.99877 | 1.0161 | 1.0338 | 1.0456 | 1.0516 | 1.0696 | 1.0879 | 1.1064
| 37 | 0.61494 | 0.64036 | 0.65454 | 0.66685 | 0.71453 | 0.76849 | 0.91915 | 0.93545 | 0.95199 | 0.96874 | 0.97439 | 0.98572 | 1.0029 | 1.0204 | 1.0321 | 1.038 | 1.0559 | 1.074 | 1.0923
| 38 | 0.60627 | 0.63129 | 0.64527 | 0.65741 | 0.70443 | 0.75769 | 0.90662 | 0.92275 | 0.93911 | 0.95569 | 0.96128 | 0.9725 | 0.98953 | 1.0068 | 1.0184 | 1.0243 | 1.042 | 1.0599 | 1.0781
| 39 | 0.59741 | 0.62205 | 0.63582 | 0.64778 | 0.69415 | 0.74672 | 0.89391 | 0.90987 | 0.92605 | 0.94246 | 0.948 | 0.9591 | 0.97596 | 0.99304 | 1.0045 | 1.0104 | 1.0279 | 1.0457 | 1.0636
| 40 | 0.58838 | 0.61264 | 0.6262 | 0.63798 | 0.68369 | 0.73557 | 0.88103 | 0.89681 | 0.91282 | 0.92906 | 0.93453 | 0.94552 | 0.96221 | 0.97912 | 0.99051 | 0.99626 | 1.0136 | 1.0312 | 1.049
| 45 | 0.54056 | 0.56289 | 0.57541 | 0.58631 | 0.62875 | 0.67715 | 0.81395 | 0.82887 | 0.84401 | 0.85938 | 0.86456 | 0.87497 | 0.89079 | 0.90684 | 0.91765 | 0.92311 | 0.93961 | 0.95633 | 0.97327
| 51.67 | 0.46987 | 0.48963 | 0.50077 | 0.51049 | 0.54855 | 0.59234 | 0.71757 | 0.73133 | 0.74532 | 0.75953 | 0.76433 | 0.77397 | 0.78863 | 0.80352 | 0.81356 | 0.81864 | 0.83397 | 0.84954 | 0.86533
y = Tconde, water returning from condensing tower
x = Tcwls, chilled water leaving temperature setpoint [C]
WaterCooled_PositiveDisplacement_Chiller_GT150_2010_PathA_CAPFT
x
|  | -6.111 | -5 | -3.889 | -3 | -2 | 0 | 5 | 5.5 | 6 | 6.5 | 6.667 | 7 | 7.5 | 8 | 8.333 | 8.5 | 9 | 9.5 | 10
y | 4.44 | 0.70779 | 0.74476 | 0.76436 | 0.78081 | 0.84011 | 0.90002 | 1.037 | 1.0497 | 1.0623 | 1.0746 | 1.0787 | 1.0867 | 1.0987 | 1.1105 | 1.1183 | 1.1221 | 1.1335 | 1.1448 | 1.1558
| 5 | 0.70677 | 0.74374 | 0.76334 | 0.77978 | 0.83908 | 0.899 | 1.036 | 1.0487 | 1.0612 | 1.0736 | 1.0776 | 1.0857 | 1.0977 | 1.1095 | 1.1172 | 1.1211 | 1.1325 | 1.1437 | 1.1548
| 7 | 0.70265 | 0.73963 | 0.75922 | 0.77567 | 0.83497 | 0.89488 | 1.0319 | 1.0446 | 1.0571 | 1.0695 | 1.0735 | 1.0816 | 1.0936 | 1.1054 | 1.1131 | 1.117 | 1.1284 | 1.1396 | 1.1507
| 9 | 0.69782 | 0.73479 | 0.75438 | 0.77083 | 0.83013 | 0.89005 | 1.0271 | 1.0398 | 1.0523 | 1.0646 | 1.0687 | 1.0768 | 1.0887 | 1.1005 | 1.1083 | 1.1121 | 1.1236 | 1.1348 | 1.1459
| 11 | 0.69225 | 0.72923 | 0.74882 | 0.76527 | 0.82457 | 0.88448 | 1.0215 | 1.0342 | 1.0467 | 1.0591 | 1.0631 | 1.0712 | 1.0832 | 1.095 | 1.1027 | 1.1066 | 1.118 | 1.1292 | 1.1403
| 13 | 0.68597 | 0.72294 | 0.74254 | 0.75898 | 0.81828 | 0.8782 | 1.0152 | 1.0279 | 1.0404 | 1.0528 | 1.0568 | 1.0649 | 1.0769 | 1.0887 | 1.0964 | 1.1003 | 1.1117 | 1.1229 | 1.134
| 14 | 0.68255 | 0.71953 | 0.73912 | 0.75557 | 0.81487 | 0.87478 | 1.0118 | 1.0245 | 1.037 | 1.0494 | 1.0534 | 1.0615 | 1.0735 | 1.0853 | 1.093 | 1.0969 | 1.1083 | 1.1195 | 1.1306
| 15 | 0.67896 | 0.71593 | 0.73553 | 0.75197 | 0.81127 | 0.87119 | 1.0082 | 1.0209 | 1.0334 | 1.0458 | 1.0498 | 1.0579 | 1.0699 | 1.0817 | 1.0894 | 1.0933 | 1.1047 | 1.1159 | 1.127
| 16 | 0.67518 | 0.71216 | 0.73175 | 0.7482 | 0.8075 | 0.86741 | 1.0044 | 1.0171 | 1.0296 | 1.042 | 1.0461 | 1.0541 | 1.0661 | 1.0779 | 1.0856 | 1.0895 | 1.1009 | 1.1122 | 1.1232
| 17.78 | 0.66801 | 0.70499 | 0.72458 | 0.74103 | 0.80033 | 0.86024 | 0.99726 | 1.01 | 1.0225 | 1.0348 | 1.0389 | 1.047 | 1.0589 | 1.0707 | 1.0785 | 1.0823 | 1.0938 | 1.105 | 1.116
| 18 | 0.66709 | 0.70406 | 0.72365 | 0.7401 | 0.7994 | 0.85932 | 0.99634 | 1.009 | 1.0216 | 1.0339 | 1.038 | 1.046 | 1.058 | 1.0698 | 1.0775 | 1.0814 | 1.0928 | 1.1041 | 1.1151
| 19 | 0.66277 | 0.69974 | 0.71933 | 0.73578 | 0.79508 | 0.855 | 0.99202 | 1.0047 | 1.0172 | 1.0296 | 1.0336 | 1.0417 | 1.0537 | 1.0655 | 1.0732 | 1.0771 | 1.0885 | 1.0997 | 1.1108
| 20 | 0.65827 | 0.69524 | 0.71483 | 0.73128 | 0.79058 | 0.8505 | 0.98752 | 1.0002 | 1.0127 | 1.0251 | 1.0291 | 1.0372 | 1.0492 | 1.061 | 1.0687 | 1.0726 | 1.084 | 1.0952 | 1.1063
| 21 | 0.65359 | 0.69056 | 0.71015 | 0.7266 | 0.7859 | 0.84582 | 0.98284 | 0.99554 | 1.0081 | 1.0204 | 1.0245 | 1.0325 | 1.0445 | 1.0563 | 1.064 | 1.0679 | 1.0793 | 1.0906 | 1.1016
| 22 | 0.64872 | 0.6857 | 0.70529 | 0.72174 | 0.78104 | 0.84095 | 0.97797 | 0.99067 | 1.0032 | 1.0155 | 1.0196 | 1.0277 | 1.0396 | 1.0514 | 1.0592 | 1.063 | 1.0745 | 1.0857 | 1.0968
| 23 | 0.64368 | 0.68065 | 0.70025 | 0.7167 | 0.776 | 0.83591 | 0.97293 | 0.98563 | 0.99815 | 1.0105 | 1.0146 | 1.0226 | 1.0346 | 1.0464 | 1.0541 | 1.058 | 1.0694 | 1.0807 | 1.0917
| 24 | 0.63846 | 0.67543 | 0.69502 | 0.71147 | 0.77077 | 0.83069 | 0.96771 | 0.98041 | 0.99292 | 1.0053 | 1.0093 | 1.0174 | 1.0294 | 1.0412 | 1.0489 | 1.0528 | 1.0642 | 1.0754 | 1.0865
| 25 | 0.63305 | 0.67002 | 0.68962 | 0.70607 | 0.76537 | 0.82528 | 0.9623 | 0.975 | 0.98752 | 0.99985 | 1.0039 | 1.012 | 1.024 | 1.0358 | 1.0435 | 1.0474 | 1.0588 | 1.07 | 1.0811
| 26 | 0.62746 | 0.66444 | 0.68403 | 0.70048 | 0.75978 | 0.81969 | 0.95671 | 0.96941 | 0.98193 | 0.99427 | 0.99834 | 1.0064 | 1.0184 | 1.0302 | 1.0379 | 1.0418 | 1.0532 | 1.0644 | 1.0755
| 27 | 0.6217 | 0.65867 | 0.67826 | 0.69471 | 0.75401 | 0.81393 | 0.95095 | 0.96365 | 0.97616 | 0.9885 | 0.99258 | 1.0006 | 1.0126 | 1.0244 | 1.0322 | 1.036 | 1.0474 | 1.0587 | 1.0697
| 28 | 0.61575 | 0.65272 | 0.67232 | 0.68876 | 0.74806 | 0.80798 | 0.945 | 0.9577 | 0.97021 | 0.98255 | 0.98663 | 0.9947 | 1.0067 | 1.0185 | 1.0262 | 1.0301 | 1.0415 | 1.0527 | 1.0638
| 29 | 0.60962 | 0.64659 | 0.66619 | 0.68263 | 0.74193 | 0.80185 | 0.93887 | 0.95157 | 0.96409 | 0.97642 | 0.9805 | 0.98857 | 1.0005 | 1.0123 | 1.0201 | 1.0239 | 1.0354 | 1.0466 | 1.0577
| 30 | 0.60331 | 0.64028 | 0.65988 | 0.67632 | 0.73562 | 0.79554 | 0.93256 | 0.94526 | 0.95778 | 0.97011 | 0.97419 | 0.98226 | 0.99423 | 1.006 | 1.0138 | 1.0176 | 1.029 | 1.0403 | 1.0513
| 31 | 0.59682 | 0.63379 | 0.65338 | 0.66983 | 0.72913 | 0.78905 | 0.92607 | 0.93877 | 0.95128 | 0.96362 | 0.9677 | 0.97577 | 0.98774 | 0.99953 | 1.0073 | 1.0111 | 1.0226 | 1.0338 | 1.0449
| 32 | 0.59014 | 0.62712 | 0.64671 | 0.66316 | 0.72246 | 0.78237 | 0.9194 | 0.93209 | 0.94461 | 0.95695 | 0.96102 | 0.9691 | 0.98107 | 0.99286 | 1.0006 | 1.0045 | 1.0159 | 1.0271 | 1.0382
| 33 | 0.58329 | 0.62026 | 0.63986 | 0.65631 | 0.71561 | 0.77552 | 0.91254 | 0.92524 | 0.93776 | 0.95009 | 0.95417 | 0.96224 | 0.97421 | 0.986 | 0.99375 | 0.99761 | 1.009 | 1.0203 | 1.0313
| 34 | 0.57626 | 0.61323 | 0.63282 | 0.64927 | 0.70857 | 0.76849 | 0.90551 | 0.91821 | 0.93072 | 0.94306 | 0.94714 | 0.95521 | 0.96718 | 0.97897 | 0.98672 | 0.99057 | 1.002 | 1.0132 | 1.0243
| 35 | 0.56904 | 0.60602 | 0.62561 | 0.64206 | 0.70136 | 0.76127 | 0.89829 | 0.91099 | 0.92351 | 0.93584 | 0.93992 | 0.94799 | 0.95996 | 0.97175 | 0.9795 | 0.98336 | 0.99478 | 1.006 | 1.0171
| 36 | 0.56164 | 0.59862 | 0.61821 | 0.63466 | 0.69396 | 0.75387 | 0.8909 | 0.90359 | 0.91611 | 0.92845 | 0.93253 | 0.9406 | 0.95257 | 0.96436 | 0.9721 | 0.97596 | 0.98738 | 0.99862 | 1.0097
| 37 | 0.55407 | 0.59104 | 0.61063 | 0.62708 | 0.68638 | 0.7463 | 0.88332 | 0.89602 | 0.90853 | 0.92087 | 0.92495 | 0.93302 | 0.94499 | 0.95678 | 0.96453 | 0.96838 | 0.97981 | 0.99105 | 1.0021
| 38 | 0.54631 | 0.58328 | 0.60288 | 0.61932 | 0.67862 | 0.73854 | 0.87556 | 0.88826 | 0.90078 | 0.91311 | 0.91719 | 0.92526 | 0.93723 | 0.94902 | 0.95677 | 0.96062 | 0.97205 | 0.98329 | 0.99435
| 39 | 0.53837 | 0.57534 | 0.59494 | 0.61138 | 0.67069 | 0.7306 | 0.86762 | 0.88032 | 0.89284 | 0.90517 | 0.90925 | 0.91732 | 0.92929 | 0.94108 | 0.94883 | 0.95269 | 0.96411 | 0.97535 | 0.98641
| 40 | 0.53025 | 0.56722 | 0.58682 | 0.60326 | 0.66256 | 0.72248 | 0.8595 | 0.8722 | 0.88472 | 0.89705 | 0.90113 | 0.9092 | 0.92117 | 0.93296 | 0.94071 | 0.94456 | 0.95599 | 0.96723 | 0.97829
| 45 | 0.48693 | 0.52391 | 0.5435 | 0.55995 | 0.61925 | 0.67916 | 0.81618 | 0.82888 | 0.8414 | 0.85373 | 0.85781 | 0.86589 | 0.87786 | 0.88964 | 0.89739 | 0.90125 | 0.91267 | 0.92391 | 0.93497
| 46.12 | 0.47661 | 0.51358 | 0.53318 | 0.54962 | 0.60892 | 0.66884 | 0.80586 | 0.81856 | 0.83108 | 0.84341 | 0.84749 | 0.85556 | 0.86753 | 0.87932 | 0.88707 | 0.89092 | 0.90235 | 0.91359 | 0.92465
Note on H8: Heine, Karl: Yellow background indicates invalid curve input values; but are shown for conditions experienced by the model
Note on Q8: Heine, Karl: Bold outline marks range of operating conditions experienced by model.
Note on U8: Heine, Karl: Green background indicates valid input values (between min/max ranges)
Note on E9: Heine, Karl: During a mid-February charging event, these extreme conditions were experienced. The value returned by the performance curve was 1.169. This confirms that E+ adjusted the inputs to minimums before evaluating the curve (as expected from a cursory look at the source code).
Note on C30: Heine, Karl: This mid-summer charging event would produce a derate to just below 70% nominal capacity. Instead we get 1.03 -> a 3% increase!
Note on M81: Heine, Karl: Reference Conditions for Model (Chiller:Electric:EIR object). Expect value of 1.0.

## EIRFT
EIRFT Curve Data Tables
y = Tconde, entering (to condenser) outdoor air drybulb temperature [C]
x = Tcwl, chilled water leaving temperature [C]
AirCooled_Chiller_2010_PathA_EIRFT
x
|  | -6.111 | -5 | -4.4 | -3.89 | -2 | 0 | 5 | 5.5 | 6 | 6.5 | 6.667 | 7 | 7.5 | 8 | 8.333 | 8.5 | 9 | 9.5 | 10
| 0 | 0.68645 | 0.66566 | 0.65524 | 0.64683 | 0.61925 | 0.59619 | 0.56616 | 0.56533 | 0.56489 | 0.56485 | 0.56492 | 0.5652 | 0.56594 | 0.56708 | 0.56805 | 0.56861 | 0.57054 | 0.57286 | 0.57558
| 2 | 0.69862 | 0.67613 | 0.6648 | 0.65561 | 0.62515 | 0.59904 | 0.56139 | 0.5598 | 0.55859 | 0.55779 | 0.55761 | 0.55737 | 0.55736 | 0.55773 | 0.5582 | 0.5585 | 0.55967 | 0.56123 | 0.56318
y | 4.44 | 0.71875 | 0.69419 | 0.68174 | 0.67161 | 0.63763 | 0.6078 | 0.56085 | 0.55833 | 0.55619 | 0.55446 | 0.55396 | 0.55311 | 0.55217 | 0.55161 | 0.55146 | 0.55145 | 0.55169 | 0.55232 | 0.55334
| 5 | 0.72418 | 0.69916 | 0.68645 | 0.6761 | 0.64131 | 0.61063 | 0.56155 | 0.55881 | 0.55646 | 0.55451 | 0.55395 | 0.55296 | 0.55179 | 0.55103 | 0.55073 | 0.55065 | 0.55067 | 0.55109 | 0.5519
| 7 | 0.7461 | 0.71938 | 0.70576 | 0.69463 | 0.65696 | 0.62323 | 0.56652 | 0.56302 | 0.55992 | 0.5572 | 0.55638 | 0.55488 | 0.55296 | 0.55143 | 0.55063 | 0.5503 | 0.54955 | 0.54921 | 0.54926
| 9 | 0.77192 | 0.74351 | 0.72897 | 0.71706 | 0.67651 | 0.63973 | 0.5754 | 0.57114 | 0.56727 | 0.56379 | 0.56272 | 0.56071 | 0.55803 | 0.55574 | 0.55443 | 0.55384 | 0.55233 | 0.55123 | 0.55051
| 11 | 0.80164 | 0.77153 | 0.75608 | 0.74339 | 0.69996 | 0.66014 | 0.58818 | 0.58315 | 0.57852 | 0.57429 | 0.57296 | 0.57044 | 0.56699 | 0.56394 | 0.56212 | 0.56128 | 0.55901 | 0.55714 | 0.55567
| 12.7 | 0.82996 | 0.79842 | 0.78219 | 0.76884 | 0.72296 | 0.68054 | 0.60211 | 0.59643 | 0.59115 | 0.58627 | 0.58473 | 0.58178 | 0.57768 | 0.57398 | 0.57173 | 0.57067 | 0.56776 | 0.56524 | 0.56311
| 14 | 0.85353 | 0.82088 | 0.80406 | 0.7902 | 0.74245 | 0.69805 | 0.61466 | 0.60849 | 0.60272 | 0.59734 | 0.59563 | 0.59235 | 0.58776 | 0.58356 | 0.58098 | 0.57976 | 0.57635 | 0.57333 | 0.57071
| 15 | 0.87277 | 0.83928 | 0.822 | 0.80776 | 0.75856 | 0.71264 | 0.62544 | 0.61889 | 0.61273 | 0.60697 | 0.60513 | 0.6016 | 0.59663 | 0.59205 | 0.58922 | 0.58786 | 0.58407 | 0.58068 | 0.57768
| 16 | 0.89299 | 0.85865 | 0.84092 | 0.82629 | 0.77565 | 0.7282 | 0.63719 | 0.63026 | 0.62372 | 0.61758 | 0.61561 | 0.61183 | 0.60647 | 0.60151 | 0.59843 | 0.59695 | 0.59278 | 0.589 | 0.58562
| 17 | 0.91419 | 0.879 | 0.86081 | 0.84579 | 0.79371 | 0.74474 | 0.64992 | 0.6426 | 0.63568 | 0.62916 | 0.62707 | 0.62303 | 0.61729 | 0.61195 | 0.60861 | 0.60701 | 0.60245 | 0.5983 | 0.59453
| 18 | 0.93636 | 0.90033 | 0.88168 | 0.86627 | 0.81275 | 0.76225 | 0.66362 | 0.65592 | 0.64862 | 0.64172 | 0.6395 | 0.63521 | 0.62909 | 0.62337 | 0.61978 | 0.61804 | 0.61311 | 0.60857 | 0.60442
| 19 | 0.95951 | 0.92263 | 0.90352 | 0.88772 | 0.83276 | 0.78074 | 0.67829 | 0.67022 | 0.66254 | 0.65525 | 0.6529 | 0.64836 | 0.64186 | 0.63576 | 0.63191 | 0.63005 | 0.62473 | 0.61981 | 0.61529
| 20 | 0.98363 | 0.9459 | 0.92634 | 0.91015 | 0.85375 | 0.8002 | 0.69395 | 0.68549 | 0.67743 | 0.66976 | 0.66729 | 0.66249 | 0.65561 | 0.64912 | 0.64502 | 0.64303 | 0.63734 | 0.63203 | 0.62713
| 21 | 1.0087 | 0.97015 | 0.95013 | 0.93355 | 0.87571 | 0.82064 | 0.71057 | 0.70173 | 0.69329 | 0.68524 | 0.68264 | 0.67759 | 0.67033 | 0.66346 | 0.65911 | 0.65699 | 0.65091 | 0.64523 | 0.63994
| 22 | 1.0348 | 0.99538 | 0.97489 | 0.95793 | 0.89865 | 0.84205 | 0.72817 | 0.71895 | 0.71013 | 0.7017 | 0.69897 | 0.69366 | 0.68602 | 0.67878 | 0.67417 | 0.67192 | 0.66547 | 0.6594 | 0.65373
| 23 | 1.0618 | 1.0216 | 1.0006 | 0.98329 | 0.92256 | 0.86444 | 0.74675 | 0.73715 | 0.72794 | 0.71913 | 0.71628 | 0.71072 | 0.70269 | 0.69507 | 0.6902 | 0.68783 | 0.68099 | 0.67455 | 0.6685
| 24 | 1.0899 | 1.0487 | 1.0274 | 1.0096 | 0.94745 | 0.88781 | 0.7663 | 0.75632 | 0.74673 | 0.73754 | 0.73456 | 0.72874 | 0.72034 | 0.71233 | 0.70722 | 0.70472 | 0.6975 | 0.69067 | 0.68424
| 25 | 1.1189 | 1.0769 | 1.055 | 1.0369 | 0.97331 | 0.91214 | 0.78683 | 0.77647 | 0.7665 | 0.75692 | 0.75381 | 0.74775 | 0.73896 | 0.73057 | 0.7252 | 0.72257 | 0.71497 | 0.70777 | 0.70095
| 26 | 1.1488 | 1.106 | 1.0837 | 1.0652 | 1.0002 | 0.93746 | 0.80833 | 0.79759 | 0.78724 | 0.77728 | 0.77405 | 0.76772 | 0.75856 | 0.74979 | 0.74416 | 0.74141 | 0.73343 | 0.72584 | 0.71864
| 27 | 1.1798 | 1.1361 | 1.1134 | 1.0944 | 1.028 | 0.96375 | 0.83081 | 0.81968 | 0.80895 | 0.79862 | 0.79525 | 0.78867 | 0.77913 | 0.76997 | 0.7641 | 0.76122 | 0.75285 | 0.74488 | 0.73731
| 28 | 1.2117 | 1.1672 | 1.144 | 1.1247 | 1.0568 | 0.99101 | 0.85426 | 0.84275 | 0.83164 | 0.82092 | 0.81743 | 0.8106 | 0.80067 | 0.79114 | 0.78501 | 0.782 | 0.77326 | 0.7649 | 0.75695
| 29 | 1.2446 | 1.1992 | 1.1756 | 1.1559 | 1.0865 | 1.0192 | 0.87868 | 0.8668 | 0.85531 | 0.84421 | 0.84059 | 0.8335 | 0.82319 | 0.81328 | 0.80689 | 0.80376 | 0.79463 | 0.7859 | 0.77756
| 30 | 1.2785 | 1.2323 | 1.2081 | 1.1881 | 1.1173 | 1.0485 | 0.90409 | 0.89182 | 0.87994 | 0.86847 | 0.86472 | 0.85738 | 0.84669 | 0.83639 | 0.82976 | 0.82649 | 0.81698 | 0.80787 | 0.79915
| 31 | 1.3133 | 1.2663 | 1.2417 | 1.2212 | 1.149 | 1.0786 | 0.93046 | 0.91781 | 0.90556 | 0.8937 | 0.88983 | 0.88223 | 0.87116 | 0.86048 | 0.85359 | 0.8502 | 0.84031 | 0.83082 | 0.82172
| 32 | 1.3491 | 1.3012 | 1.2762 | 1.2553 | 1.1817 | 1.1098 | 0.95781 | 0.94478 | 0.93215 | 0.91991 | 0.91591 | 0.90806 | 0.89661 | 0.88555 | 0.8784 | 0.87488 | 0.86461 | 0.85474 | 0.84526
| 33 | 1.3859 | 1.3372 | 1.3117 | 1.2904 | 1.2153 | 1.1419 | 0.98614 | 0.97273 | 0.95971 | 0.94709 | 0.94296 | 0.93486 | 0.92303 | 0.91159 | 0.90419 | 0.90054 | 0.88989 | 0.87964 | 0.86977
| 34 | 1.4237 | 1.3741 | 1.3482 | 1.3265 | 1.25 | 1.1751 | 1.0154 | 1.0017 | 0.98825 | 0.97525 | 0.97099 | 0.96264 | 0.95042 | 0.9386 | 0.93095 | 0.92718 | 0.91614 | 0.90551 | 0.89526
| 35 | 1.4625 | 1.412 | 1.3856 | 1.3636 | 1.2856 | 1.2091 | 1.0457 | 1.0315 | 1.0178 | 1.0044 | 1 | 0.99139 | 0.97879 | 0.96659 | 0.95868 | 0.95478 | 0.94337 | 0.93235 | 0.92173
| 36 | 1.5022 | 1.4509 | 1.424 | 1.4016 | 1.3222 | 1.2442 | 1.077 | 1.0624 | 1.0483 | 1.0345 | 1.03 | 1.0211 | 1.0081 | 0.99556 | 0.9874 | 0.98337 | 0.97157 | 0.96017 | 0.94917
| 37 | 1.5429 | 1.4907 | 1.4634 | 1.4406 | 1.3597 | 1.2803 | 1.1092 | 1.0943 | 1.0797 | 1.0656 | 1.0609 | 1.0518 | 1.0385 | 1.0255 | 1.0171 | 1.0129 | 1.0008 | 0.98897 | 0.97758
| 38 | 1.5845 | 1.5316 | 1.5038 | 1.4806 | 1.3983 | 1.3173 | 1.1424 | 1.1271 | 1.1122 | 1.0976 | 1.0929 | 1.0835 | 1.0698 | 1.0564 | 1.0477 | 1.0435 | 1.0309 | 1.0187 | 1.007
| 39 | 1.6272 | 1.5734 | 1.5451 | 1.5215 | 1.4378 | 1.3553 | 1.1766 | 1.1609 | 1.1456 | 1.1307 | 1.1258 | 1.1161 | 1.102 | 1.0883 | 1.0794 | 1.075 | 1.062 | 1.0495 | 1.0373
| 40 | 1.6708 | 1.6161 | 1.5874 | 1.5635 | 1.4783 | 1.3942 | 1.2117 | 1.1956 | 1.18 | 1.1647 | 1.1597 | 1.1498 | 1.1353 | 1.1212 | 1.112 | 1.1075 | 1.0941 | 1.0812 | 1.0687
| 45 | 1.9035 | 1.8446 | 1.8136 | 1.7877 | 1.6953 | 1.6037 | 1.4021 | 1.3841 | 1.3665 | 1.3493 | 1.3437 | 1.3325 | 1.3161 | 1.3001 | 1.2897 | 1.2845 | 1.2693 | 1.2544 | 1.24
| 51.67 | 2.252 | 2.1874 | 2.1534 | 2.1249 | 2.0228 | 1.921 | 1.694 | 1.6735 | 1.6534 | 1.6336 | 1.6271 | 1.6143 | 1.5953 | 1.5768 | 1.5646 | 1.5586 | 1.5409 | 1.5235 | 1.5065
y = Tconde, water returning from condensing tower [C]
x = Tcwl, chilled water leaving temperature [C]
WaterCooled_PositiveDisplacement_Chiller_GT150_2010_PathA_EIRFT
x
|  | -6.111 | -5 | -3.889 | -3 | -2 | 0 | 5 | 5.5 | 6 | 6.5 | 6.667 | 7 | 7.5 | 8 | 8.333 | 8.5 | 9 | 9.5 | 10
y | 4.44 | 0.63993 | 0.59411 | 0.57106 | 0.55241 | 0.49075 | 0.43834 | 0.36508 | 0.3623 | 0.36033 | 0.3592 | 0.359 | 0.35889 | 0.3594 | 0.36074 | 0.36209 | 0.3629 | 0.36589 | 0.36971 | 0.37435
| 5 | 0.64885 | 0.60303 | 0.57998 | 0.56132 | 0.49966 | 0.44725 | 0.374 | 0.37121 | 0.36925 | 0.36811 | 0.36791 | 0.3678 | 0.36831 | 0.36965 | 0.371 | 0.37182 | 0.37481 | 0.37862 | 0.38326
| 7 | 0.68291 | 0.63709 | 0.61404 | 0.59538 | 0.53372 | 0.48131 | 0.40806 | 0.40527 | 0.40331 | 0.40217 | 0.40197 | 0.40186 | 0.40237 | 0.40371 | 0.40506 | 0.40588 | 0.40886 | 0.41268 | 0.41732
| 9 | 0.72044 | 0.67462 | 0.65157 | 0.63291 | 0.57125 | 0.51885 | 0.44559 | 0.4428 | 0.44084 | 0.43971 | 0.43951 | 0.43939 | 0.43991 | 0.44125 | 0.4426 | 0.44341 | 0.4464 | 0.45021 | 0.45485
| 11 | 0.76145 | 0.71563 | 0.69258 | 0.67393 | 0.61227 | 0.55986 | 0.4866 | 0.48381 | 0.48185 | 0.48072 | 0.48052 | 0.4804 | 0.48092 | 0.48226 | 0.48361 | 0.48442 | 0.48741 | 0.49123 | 0.49587
| 13 | 0.80594 | 0.76012 | 0.73707 | 0.71841 | 0.65675 | 0.60434 | 0.53109 | 0.5283 | 0.52634 | 0.5252 | 0.52501 | 0.52489 | 0.52541 | 0.52674 | 0.52809 | 0.52891 | 0.5319 | 0.53571 | 0.54035
| 14 | 0.82949 | 0.78367 | 0.76062 | 0.74196 | 0.6803 | 0.62789 | 0.55464 | 0.55185 | 0.54989 | 0.54875 | 0.54855 | 0.54844 | 0.54895 | 0.55029 | 0.55164 | 0.55246 | 0.55545 | 0.55926 | 0.5639
| 15 | 0.8539 | 0.80808 | 0.78503 | 0.76638 | 0.70472 | 0.65231 | 0.57905 | 0.57627 | 0.5743 | 0.57317 | 0.57297 | 0.57286 | 0.57337 | 0.57471 | 0.57606 | 0.57687 | 0.57986 | 0.58368 | 0.58832
| 16 | 0.87919 | 0.83337 | 0.81032 | 0.79166 | 0.73 | 0.67759 | 0.60434 | 0.60155 | 0.59959 | 0.59845 | 0.59826 | 0.59814 | 0.59865 | 0.59999 | 0.60134 | 0.60216 | 0.60515 | 0.60896 | 0.6136
| 17.78 | 0.92635 | 0.88053 | 0.85748 | 0.83882 | 0.77716 | 0.72475 | 0.65149 | 0.64871 | 0.64675 | 0.64561 | 0.64541 | 0.6453 | 0.64581 | 0.64715 | 0.6485 | 0.64931 | 0.6523 | 0.65612 | 0.66076
| 18 | 0.93236 | 0.88655 | 0.8635 | 0.84484 | 0.78318 | 0.73077 | 0.65751 | 0.65473 | 0.65277 | 0.65163 | 0.65143 | 0.65132 | 0.65183 | 0.65317 | 0.65452 | 0.65533 | 0.65832 | 0.66214 | 0.66678
| 19 | 0.96026 | 0.91444 | 0.89139 | 0.87273 | 0.81107 | 0.75866 | 0.68541 | 0.68262 | 0.68066 | 0.67952 | 0.67933 | 0.67921 | 0.67972 | 0.68106 | 0.68241 | 0.68323 | 0.68622 | 0.69003 | 0.69467
| 20 | 0.98902 | 0.9432 | 0.92015 | 0.90149 | 0.83983 | 0.78742 | 0.71417 | 0.71138 | 0.70942 | 0.70828 | 0.70809 | 0.70797 | 0.70848 | 0.70982 | 0.71117 | 0.71199 | 0.71498 | 0.71879 | 0.72343
| 21 | 1.0186 | 0.97283 | 0.94978 | 0.93112 | 0.86946 | 0.81705 | 0.7438 | 0.74101 | 0.73905 | 0.73791 | 0.73772 | 0.7376 | 0.73811 | 0.73945 | 0.7408 | 0.74162 | 0.74461 | 0.74842 | 0.75306
| 22 | 1.0491 | 1.0033 | 0.98028 | 0.96162 | 0.89996 | 0.84755 | 0.7743 | 0.77151 | 0.76955 | 0.76841 | 0.76822 | 0.7681 | 0.76861 | 0.76995 | 0.7713 | 0.77212 | 0.77511 | 0.77892 | 0.78356
| 23 | 1.0805 | 1.0347 | 1.0116 | 0.99299 | 0.93133 | 0.87892 | 0.80566 | 0.80288 | 0.80092 | 0.79978 | 0.79958 | 0.79947 | 0.79998 | 0.80132 | 0.80267 | 0.80349 | 0.80647 | 0.81029 | 0.81493
| 24 | 1.1128 | 1.0669 | 1.0439 | 1.0252 | 0.96357 | 0.91116 | 0.8379 | 0.83511 | 0.83315 | 0.83202 | 0.83182 | 0.83171 | 0.83222 | 0.83356 | 0.83491 | 0.83572 | 0.83871 | 0.84253 | 0.84717
| 25 | 1.1459 | 1.1 | 1.077 | 1.0583 | 0.99667 | 0.94426 | 0.87101 | 0.86822 | 0.86626 | 0.86512 | 0.86493 | 0.86481 | 0.86533 | 0.86666 | 0.86801 | 0.86883 | 0.87182 | 0.87563 | 0.88027
| 26 | 1.1798 | 1.134 | 1.111 | 1.0923 | 1.0306 | 0.97824 | 0.90498 | 0.9022 | 0.90023 | 0.8991 | 0.8989 | 0.89879 | 0.8993 | 0.90064 | 0.90199 | 0.9028 | 0.90579 | 0.90961 | 0.91425
| 27 | 1.2147 | 1.1689 | 1.1458 | 1.1272 | 1.0655 | 1.0131 | 0.93983 | 0.93704 | 0.93508 | 0.93394 | 0.93375 | 0.93363 | 0.93414 | 0.93548 | 0.93683 | 0.93765 | 0.94064 | 0.94445 | 0.94909
| 28 | 1.2504 | 1.2046 | 1.1815 | 1.1629 | 1.1012 | 1.0488 | 0.97554 | 0.97275 | 0.97079 | 0.96965 | 0.96946 | 0.96934 | 0.96986 | 0.9712 | 0.97255 | 0.97336 | 0.97635 | 0.98016 | 0.9848
| 29 | 1.287 | 1.2412 | 1.2181 | 1.1994 | 1.1378 | 1.0854 | 1.0121 | 1.0093 | 1.0074 | 1.0062 | 1.006 | 1.0059 | 1.0064 | 1.0078 | 1.0091 | 1.0099 | 1.0129 | 1.0167 | 1.0214
| 30 | 1.3244 | 1.2786 | 1.2556 | 1.2369 | 1.1752 | 1.1228 | 1.0496 | 1.0468 | 1.0448 | 1.0437 | 1.0435 | 1.0434 | 1.0439 | 1.0452 | 1.0466 | 1.0474 | 1.0504 | 1.0542 | 1.0588
| 31 | 1.3627 | 1.3169 | 1.2939 | 1.2752 | 1.2136 | 1.1611 | 1.0879 | 1.0851 | 1.0831 | 1.082 | 1.0818 | 1.0817 | 1.0822 | 1.0835 | 1.0849 | 1.0857 | 1.0887 | 1.0925 | 1.0972
| 32 | 1.4019 | 1.3561 | 1.3331 | 1.3144 | 1.2527 | 1.2003 | 1.1271 | 1.1243 | 1.1223 | 1.1212 | 1.121 | 1.1209 | 1.1214 | 1.1227 | 1.1241 | 1.1249 | 1.1279 | 1.1317 | 1.1363
| 33 | 1.442 | 1.3962 | 1.3731 | 1.3545 | 1.2928 | 1.2404 | 1.1671 | 1.1644 | 1.1624 | 1.1613 | 1.1611 | 1.1609 | 1.1615 | 1.1628 | 1.1641 | 1.165 | 1.168 | 1.1718 | 1.1764
| 34 | 1.4829 | 1.4371 | 1.414 | 1.3954 | 1.3337 | 1.2813 | 1.2081 | 1.2053 | 1.2033 | 1.2022 | 1.202 | 1.2019 | 1.2024 | 1.2037 | 1.2051 | 1.2059 | 1.2089 | 1.2127 | 1.2173
| 35 | 1.5247 | 1.4789 | 1.4558 | 1.4372 | 1.3755 | 1.3231 | 1.2499 | 1.2471 | 1.2451 | 1.244 | 1.2438 | 1.2437 | 1.2442 | 1.2455 | 1.2469 | 1.2477 | 1.2507 | 1.2545 | 1.2591
| 36 | 1.5674 | 1.5216 | 1.4985 | 1.4799 | 1.4182 | 1.3658 | 1.2925 | 1.2897 | 1.2878 | 1.2866 | 1.2864 | 1.2863 | 1.2868 | 1.2882 | 1.2895 | 1.2903 | 1.2933 | 1.2972 | 1.3018
| 37 | 1.6109 | 1.5651 | 1.542 | 1.5234 | 1.4617 | 1.4093 | 1.3361 | 1.3333 | 1.3313 | 1.3302 | 1.33 | 1.3299 | 1.3304 | 1.3317 | 1.3331 | 1.3339 | 1.3369 | 1.3407 | 1.3453
| 38 | 1.6553 | 1.6095 | 1.5864 | 1.5678 | 1.5061 | 1.4537 | 1.3805 | 1.3777 | 1.3757 | 1.3746 | 1.3744 | 1.3743 | 1.3748 | 1.3761 | 1.3775 | 1.3783 | 1.3813 | 1.3851 | 1.3897
| 39 | 1.7006 | 1.6548 | 1.6317 | 1.6131 | 1.5514 | 1.499 | 1.4257 | 1.423 | 1.421 | 1.4199 | 1.4197 | 1.4195 | 1.4201 | 1.4214 | 1.4227 | 1.4236 | 1.4265 | 1.4304 | 1.435
| 40 | 1.7467 | 1.7009 | 1.6779 | 1.6592 | 1.5975 | 1.5451 | 1.4719 | 1.4691 | 1.4671 | 1.466 | 1.4658 | 1.4657 | 1.4662 | 1.4675 | 1.4689 | 1.4697 | 1.4727 | 1.4765 | 1.4811
| 45 | 1.9905 | 1.9447 | 1.9216 | 1.9029 | 1.8413 | 1.7889 | 1.7156 | 1.7128 | 1.7109 | 1.7097 | 1.7095 | 1.7094 | 1.7099 | 1.7113 | 1.7126 | 1.7134 | 1.7164 | 1.7202 | 1.7249
| 46.12 | 2.048 | 2.0022 | 1.9792 | 1.9605 | 1.8989 | 1.8465 | 1.7732 | 1.7704 | 1.7684 | 1.7673 | 1.7671 | 1.767 | 1.7675 | 1.7689 | 1.7702 | 1.771 | 1.774 | 1.7778 | 1.7825
Note on E9: Heine, Karl: Same February (extreme) event conditions. EIR multiplier lower than expected due to limits on curve inputs.
Note on C30: Heine, Karl: Same summer event. Instead of increasing our EIR multiplier 18% above nominal, we get a 17% reduction from nominal.
Note on M38: Heine, Karl: Reference Conditions
Note on M81: Heine, Karl: Reference Conditions from model. Expect value of 1.0.

## EIRPLR
EIRPLR Curve Data Tables
x = Part Load Ratio (Q_load/Q_avail = Q_load/(Q_ref*CAPFT) or PLR_max (
AirCooled_Chiller_2010_PathA_EIRPLR
x
0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
0.141 | 0.20853 | 0.28012 | 0.35577 | 0.43548 | 0.51925 | 0.60708 | 0.69897 | 0.79492 | 0.89493 | 0.999
ChlrWtrCentPathAAllEIRRatio_fQRatio
x
0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
0.22215 | 0.27503 | 0.33306 | 0.39622 | 0.46452 | 0.53795 | 0.61653 | 0.70024 | 0.78909 | 0.88308 | 0.98221
Note on K9: Heine, Karl: Oddly enough, by having the "oversized" chiller in our ice model, we aren't running at PLR = 1 during ice making only. This gives us a PLR ~.6, which gives us significant energy savings through the power calculation.
Note on A14: Heine, Karl: Out of bounds.
Note on B15: Heine, Karl: 0.28 minimum curve output value

## Example Chiller Power Calcs
Example Chiller Power Calculation for Summer Recharge Period
|  |  | CAPFT |  | EIRFT |  | EIRPLR
Tdb | Tcwls | Tcwl | Curves | Extended | Curves | Extended | Curves | Extended
31 | -5 | -5 | 0.991 | 0.691 | 1.313 | 0.93 | 0.67 | 0.97
Chiller Power Multiplier Results
|  | Curves As-Is |  | 0.87179
|  | Extended Curves |  | 0.62335
Note on H7: Heine, Karl: Estimated from DVIEW results.
Note on I7: Heine, Karl: Fractional estmation based on the PLR of the curves as-is and what would be expected from the "extended" curves.